## 2013
QUALITIES OF THE NATURAL GAS TYPES SUPPLIED IN BELGIUM
ANNUAL AVERAGES 2013
QUALITY Ref. 1 | SYMBOL | UNIT | SLOCHTEREN (10) | SEGEO (20) | LNG (29) | ZPT (91) | IZTF (34)
NATURAL GAS TYPE | Reference location |  | Poppel | s Gravenvoeren | Terminal | Ramskapelle | Zeebrugge
| Gas type |  | L – gas | H – gas | H – gas | H – gas | H – gas
GAS COMPOSITION Ref.1
Nitrogen | N2 | mol % | 13.08 | 4.268 | 1.206 | 1.082 | 2.633
Carbon dioxide | CO2 | mol % | 1.106 | 1.505 | 0.001 | 1.346 | 1.3
Methane | C1 (CH4) | mol % | 82.068 | 88.4 | 93.882 | 91.129 | 89.886
Ethane | C2 (C2H6) | mol % | 3.013 | 4.478 | 4.844 | 4.803 | 4.637
Propane | C3 (C3H8) | mol % | 0.441 | 0.907 | 0.06 | 1.049 | 1.032
Iso-butane | iC4 | mol % | 0.071 | 0.132 | 0.003 | 0.246 | 0.158
N-butane | nC4 | mol % | 0.089 | 0.15 | 0.004 | 0.164 | 0.191
Iso-pentane | iC5 | mol % | 0.02 | 0.038 | 0 | 0.054 | 0.048
N-pentane | nC5 | mol % | 0.019 | 0.033 | 0 | 0.035 | 0.041
Hexane and superior HC | C6+ | mol % | 0.047 | 0.057 | 0 | 0.077 | 0.054
Helium | He | mol % | 0.046 | 0.032 | 0 | 0.015 | 0.02
Oxygen | O2 | mol % | 0 | 0 | 0 | 0 | 0
CALCULATED VALUES Ref. 2
Gross Caloric Value | GCV | kJ /m3 (n) | 35586.9193 | 39836.7922 | 40852.4402 | 41530.622 | 40775.6677
Net Caloric Value | NCV | kJ /m3 (n) | 32117.0164 | 35975.724 | 36864.518 | 37513.5838 | 36828.2493
Gross Caloric Value | GCV | kJ /m3 (n) Min | 35063 | 39331 | 35001 | 40653 | 39706
Gross Caloric Value | GCV | kJ /m3 (n) Max | 37316 | 41379 | 42275 | 42611 | 42661
Gross Caloric Value | GCV | kWh /m3 (n) | 9.8853 | 11.0658 | 11.3479 | 11.5363 | 11.3266
Net Caloric Value | NCV | kWh /m3 (n) | 8.9214 | 9.9933 | 10.2401 | 10.4204 | 10.2301
Wobbe index (GCV/√d) | W I | kJ /m3 (n) | 44391.0396 | 50405.128 | 53446.5555 | 52927.5204 | 51818.4787
Density | RON | kg / m3 (n) | 0.83093 | 0.80759 | 0.75539 | 0.79606 | 0.80058
Relative mass density | d | - | 0.64278 | 0.62473 | 0.58435 | 0.61581 | 0.61931
Gross Caloric Value | GCV | kJ / kg | 42828.7944 | 49328.8043 | 54082.3983 | 52171.1332 | 50933.5403
Net Caloric Value | NCV | kJ / kg | 38652.4436 | 44547.3204 | 48802.6766 | 47124.4078 | 46002.2921
Ratio NCV / GCV | NCV / GCV | - | 0.90249 | 0.90308 | 0.90238 | 0.90328 | 0.90319
STOCHIOMETRIC COMBUSTION Ref. 3
Stochiometric air requirement | a (moist air) | m3 (n) air / m3 (n) gas | 8.569 | 9.5912 | 9.8391 | 9.9982 | 9.8168
Combustion prod. at stochiometric combustion (moist) | q st (moist air) | m3 (n) comb.prod. / m3 (n) gas | 9.529 | 10.5593 | 10.7908 | 10.9697 | 10.7869
Combustion prod. at stochiometric combustion (dry) | q st (dry air) | m3 (n) comb.prod. / m3 (n) gas | 7.7984 | 8.6334 | 8.8017 | 8.966 | 8.818
Comb.prod. max.CO2 | % CO2 max | % m³ / m³ | 9.5744 | 9.7534 | 9.5776 | 9.7865 | 9.7619
Comb.prod. max.CO2 | % CO2 max | # mol / mol | 0.9164 | 1.0341 | 1.0378 | 1.0777 | 1.0572
Comb.prod. max. H2O | % H2O max | % m³ / m³ | 17.8955 | 17.9696 | 18.1629 | 17.9957 | 17.9837
Dry comb.prod. max.CO2 | % CO2 max | % m³ / m³ | 11.6992 | 11.9291 | 11.742 | 11.9735 | 11.9416
ADDITIONAL DATA Ref. 3
Molar mass | Mol. Mass | kg / kmol | 18.581 | 18.052 | 16.8869 | 17.7916 | 17.894
Weight percentage C | C mass % | % | 59.2437 | 68.8082 | 73.8151 | 72.7616 | 70.9674
Weight percentage H | H mass % | % | 19.1293 | 21.9001 | 24.1824 | 23.1137 | 22.5854
Weight percentage N | N mass % | % | 19.7221 | 6.6237 | 2.0006 | 1.7037 | 4.1223
Weight percentage O | O mass % | % | 1.9049 | 2.668 | 0.0018949 | 2.4209 | 2.3249
Specific CO2 emission | - | kg CO2/GJ | 56.155 | 56.5918 | 55.42 | 56.5727 | 56.5231
Specific CO2 emission | - | kg CO2/MWh | 202.158 | 203.7303 | 199.512 | 203.6618 | 203.483
H2S Mean (ref. 1) (*) | H2S | mg/m³ (n) | 0.13848 | 1.8 | 0.4 | 2.1 | 1
H2S Max (ref.1) (*) | H2S | mg/m³ (n) | 0.8 | 5 | 5 | 4.8 | 3
Total Sulfur Mean (ref.1) (*) | S | mg/m³ (n) | 0.05922 | 1.4 | 0.2 | 1.5 | 4.1
Total Sulfur Max (ref.1) (*) | S | mg/m³ (n) | 2.2 | 8 | 3.9 | 6 | 5.4
The information above is given for information only.
Ref. [1] : Fluxys - Quality & Metrology
Ref. [2] : ISO 6976 - 1995 , reference temperature for the combustion enthalpy: 25 °C ; 1 m³ (n): at 0 °C and 1013.25 mbar
Ref. [3] : Reference temperature and pressure (0 °C and 1013.25 mbar) ; Fluxys
(*) These values are given as a trend only.
(**) These values are not significant due to the high N2 content in Slochteren gas.
Editor: Cordier L. | E-mail: laurent.cordier@fluxys.com