## 2015
QUALITIES OF THE NATURAL GAS TYPES SUPPLIED IN BELGIUM
ANNUAL AVERAGES 2015
QUALITY Ref. 1 | SYMBOL | UNIT | SLOCHTEREN (10) | SEGEO (20) | LNG (29) | IZTF (34) | ZPT (91)
NATURAL GAS TYPE | Reference location |  | Poppel | s Gravenvoeren | Terminal | Zeebrugge | Ramskapelle
| Gas type |  | L – gas | H – gas | H – gas | H – gas | H – gas
GAS COMPOSITION Ref.1
Nitrogen | N2 | mol % | 11.2465 | 1.7412 | 0.45656 | 1.769 | 1.3295
Carbon dioxide | CO2 | mol % | 1.2311 | 1.3537 | 1.7621e-05 | 1.0396 | 1.3906
Methane | C1 (CH4) | mol % | 83.1771 | 90.7767 | 93.0158 | 90.4443 | 91.2467
Ethane | C2 (C2H6) | mol % | 3.4147 | 4.8056 | 6.2992 | 5.2177 | 4.4877
Propane | C3 (C3H8) | mol % | 0.57505 | 0.89451 | 0.17891 | 1.0418 | 0.93486
Iso-butane | iC4 | mol % | 0.090536 | 0.13818 | 0.0188 | 0.15915 | 0.27959
N-butane | nC4 | mol % | 0.11249 | 0.14578 | 0.02759 | 0.17383 | 0.13969
Iso-pentane | iC5 | mol % | 0.0267 | 0.036581 | 0.0011598 | 0.042622 | 0.054683
N-pentane | nC5 | mol % | 0.024504 | 0.029309 | 0.00048611 | 0.033838 | 0.029595
Hexane and superior HC | C6+ | mol % | 0.052448 | 0.045897 | 0.0013401 | 0.053392 | 0.089978
Oxygen | O2 | mol % | 2.3345e-05 | 0 | 5.1633e-05 | 1.3992e-07 | 0
Helium | He | mol % | 0.048864 | 0.032523 | 0 | 0.024608 | 0.017093
CALCULATED VALUES Ref. 2
Gross Caloric Value | GCV | kJ /m3 (n) | 36530.8665 | 40975.6609 | 41702.1219 | 41373.4935 | 41272.8748
Net Caloric Value | NCV | kJ /m3 (n) | 32976.2577 | 37004.3004 | 37648.2628 | 37371.9866 | 37276.767
Gross Caloric Value | GCV | kJ /m3 (n) Min | 35030.31 | 39294.2 | 35120.8 | 40233.98 | 40823.15
Gross Caloric Value | GCV | kJ /m3 (n) Max | 37550.1 | 42040.61 | 43805.17 | 42618.98 | 42383.96
Gross Caloric Value | GCV | kWh /m3 (n) | 10.1475 | 11.3821 | 11.5839 | 11.4926 | 11.4647
Net Caloric Value | NCV | kWh /m3 (n) | 9.1601 | 10.279 | 10.4579 | 10.3811 | 10.3547
Wobbe index (GCV/√d) | W I | kJ /m3 (n) | 45642.6978 | 52298.3521 | 54288.8973 | 52734.6759 | 52635.414
Density | RON | kg / m3 (n) | 0.82823 | 0.79369 | 0.7629 | 0.79584 | 0.79496
Relative mass density | d | - | 0.64059 | 0.61387 | 0.59006 | 0.61553 | 0.61486
Gross Caloric Value | GCV | kJ / kg | 44108.0936 | 51628.0217 | 54663.5683 | 51988.3211 | 51919.0911
Net Caloric Value | NCV | kJ / kg | 39815.8337 | 46623.7914 | 49349.3958 | 46959.7175 | 46891.7202
Ratio NCV / GCV | NCV / GCV | - | 0.9027 | 0.90308 | 0.90279 | 0.90328 | 0.90318
STOCHIOMETRIC COMBUSTION Ref. 3
Stochiometric air requirement | a (moist air) | m3 (n) air / m3 (n) gas | 8.7958 | 9.8659 | 10.0435 | 9.9612 | 9.9361
Combustion prod. at stochiometric combustion (moist) | q st (moist air) | m3 (n) comb.prod. / m3 (n) gas | 9.7587 | 10.8331 | 11.0032 | 10.9327 | 10.9055
Combustion prod. at stochiometric combustion (dry) | q st (dry air) | m3 (n) comb.prod. / m3 (n) gas | 7.9858 | 8.8522 | 8.9811 | 8.9368 | 8.9123
Comb.prod. max.CO2 | % CO2 max | % m³ / m³ | 9.6259 | 9.7613 | 9.6268 | 9.7559 | 9.7781
Comb.prod. max.CO2 | % CO2 max | # mol / mol | 0.94346 | 1.0617 | 1.0635 | 1.0708 | 1.0706
Comb.prod. max. H2O | % H2O max | % m³ / m³ | 17.9007 | 18.0159 | 18.1068 | 17.9871 | 18.0071
Dry comb.prod. max.CO2 | % CO2 max | % m³ / m³ | 11.763 | 11.9456 | 11.7943 | 11.9349 | 11.9649
ADDITIONAL DATA Ref. 3
Molar mass | Mol. Mass | kg / kmol | 18.5189 | 17.7398 | 17.0528 | 17.7872 | 17.7676
Weight percentage C | C mass % | % | 61.1978 | 71.8875 | 74.9097 | 72.3117 | 72.3741
Weight percentage H | H mass % | % | 19.6602 | 22.9207 | 24.3401 | 23.0317 | 23.0251
Weight percentage N | N mass % | % | 17.0145 | 2.7499 | 0.75002 | 2.7863 | 2.0962
Weight percentage O | O mass % | % | 2.1275 | 2.442 | 0.00012995 | 1.8704 | 2.5046
Specific CO2 emission | - | kg CO2/GJ | 56.3119 | 56.491 | 55.6188 | 56.4188 | 56.5504
Specific CO2 emission | - | kg CO2/MWh | 202.7228 | 203.3676 | 200.2275 | 203.1078 | 203.5815
H2S Mean (ref. 1) | H2S | mg/m³ (n) | 0.6166 | 2.4911 | 0.82132 | 0.87737 | 2.1312
H2S Max (ref.1) | H2S | mg/m³ (n) | 1.5467 | 4.0987 | 4.6351 | 4.7149 | 4.9472
Total Sulfur Mean (ref.1) | S | mg/m³ (n) | 0.24574 | 1.8199 | 0.52849 | 0.79566 | 1.2827
Total Sulfur Max (ref.1) | S | mg/m³ (n) | 0.83417 | 3.1667 | 3.8002 | 4.57 | 3.3935
CH4 rate (ref.4) | AVL | (+/- 2 units) | (**) | 80.3778 | 83.3261 | 78.9689 | #VALUE!
| ISO | (+/- 2 units) | (**) | 82.4221 | 84.5044 | 80.9264 | #VALUE!
The information above is given for information only.
Ref. [1] : Fluxys - Quality & Metrology
Ref. [2] : ISO 6976 - 1995 , reference temperature for the combustion enthalpy: 25 °C ; 1 m³ (n): at 0 °C and 1013.25 mbar
Ref. [3] : Reference temperature and pressure (0 °C and 1013.25 mbar) ; Fluxys
Editor: Cordier L. | E-mail: laurent.cordier@fluxys.com